# Cooling Tower Model Documentation

Comprehensive reference for cooling tower thermodynamic parameters, wet-bulb temperature calculations, and economic correlations.

## 1. Wet-Bulb Temperature Calculation

The wet-bulb temperature (T

wb

) can be computed from dry-bulb temperature and relative humidity using the empirical formula developed by Stull (2011):

### 1.1 Stull Formula

T_wb = T · arctan[0.151977 · √(RH + 8.313659)] + arctan(T + RH) − arctan(RH − 1.676331) + 0.00391838 · RH^(3/2) · arctan(0.023101 · RH) − 4.686035

where:

- T = dry-bulb temperature (°C)

- RH = relative humidity (%)

- arctan = inverse tangent function (evaluated in radians, not degrees)

### 1.2 Validity Range and Accuracy

The Stull formula is valid for:

- Relative humidity: 5% to 99%

- Air temperature: −20°C to 50°C

- Exception: Not valid for situations with both low humidity and cold temperature

- Standard sea-level pressure (101.325 kPa)

Accuracy metrics:

- Error range: −1°C to +0.65°C

- Mean absolute error: < 0.3°C

- Fraction of variance explained (r²): 99.95%

- Mean error: −0.0052°C

- Median error: +0.026°C

### 1.3 Implementation Notes

- Critical: The atan function must be evaluated in radians, not degrees. Lua's math.atan returns radians by default.

- The formula assumes standard sea-level pressure. Errors increase at higher elevations.

- This formula is widely implemented in building energy simulation libraries (e.g., Modelica Buildings library, AixLib) and weather data APIs (e.g., Open-Meteo).

### 1.4 Reference

Stull, R. (2011). Wet-bulb temperature from relative humidity and air temperature. Journal of Applied Meteorology and Climatology, 50(11), 2267–2269.

DOI: 10.1175/JAMC-D-11-0143.1

## 2. Cooling Tower Design Guidelines

### 2.1 Typical Range and Approach Values

Industry design guidelines recommend:

- Range: 10–15°F (5.5–8.3°C) — difference between hot and cold water temperatures

- Approach: 6–12°F (3.3–6.7°C) — difference between cold water and wet-bulb temperatures

- Inlet water temperature: < 92°F (33°C)

- Modern towers commonly achieve approach temperatures as low as 5°F (~3°C)

### 2.2 Physical Constraints

- Critical: Cold water temperature cannot be cooled below the ambient wet-bulb temperature through evaporative cooling.

- Therefore, approach temperature must always be positive: Cool_Tin > T_wetbulb

- Smaller approaches require exponentially larger tower sizes, leading to diminishing returns in cost-effectiveness

### 2.3 Performance Relationships

The relationship between wet-bulb temperature and cold water temperature is approximately 2:1:

- For each 2°F drop in wet-bulb temperature, cold water temperature drops ~1°F

- The approach increases by ~1°F for every 2°F the wet-bulb falls below design conditions

- This is a rough approximation; actual performance should reference manufacturer curves or CTI Blue Book data

## 3. Model Parameters

| Parameter | Default Value | Unit | Description / Source |
| --- | --- | --- | --- |
| COOLING WATER CIRCUIT |  |  |  |
| Cool_Tin | 13 | °C | Supply temperature (updated from 12°C to ensure approach > 0) |
| Cool_Tout | 14 | °C | Return temperature (original Florez-Orrego / ECOS2105: 40°C) |
| Cool_Qmax | 100,000 | kW | Reference heat duty |
| deltaH | 62.8 | kJ/kg | Enthalpy change of cooling water @ 1 bar, 15 → 30°C |
| AMBIENT CONDITIONS |  |  |  |
| Tdrybulb | 20 | °C | Dry-bulb temperature (site-specific) |
| RelatHum | 40 | % | Relative humidity (site-specific) |
| Twetbulb | 12.17 | °C | Wet-bulb temperature (computed from Stull formula, consistent with 20°C / 40% RH) |
| ELECTRICITY |  |  |  |
| Cool_Elec | 0.021 | kW_el / kW_th | Specific electricity consumption (MARLEY; 400 tons → 30 kW) |
| HEAT INTEGRATION ΔT_min CONTRIBUTIONS |  |  |  |
| dtmin_gas | 8 | °C | Gas streams |
| dtmin_liq | 5 | °C | Liquid streams |
| dtmin_2ph | 2 | °C | Two-phase streams |
| ECONOMICS |  |  |  |
| n | 40 | year | Plant lifetime |
| i | 0.06 | — | Interest / discount rate |
| CEPCI_2020 | 596.2 | — | Chemical Engineering Plant Cost Index, 2020 |
| CEPCI_2008 | 575.4 | — | Chemical Engineering Plant Cost Index, 2008 (correlation base year) |

## 4. Calculated Values

| Name | Formula | Unit | Result | Notes |
| --- | --- | --- | --- | --- |
| THERMAL PERFORMANCE |  |  |  |  |
| range | Cool_Tout − Cool_Tin | K | 1 | Very small (typical: 5.5–8.3 K) |
| approach | Cool_Tin − Twetbulb | K | 0.83 | Now positive (typical: 3.3–6.7 K) |
| E_ref_CT | Cool_Elec × Cool_Qmax | kW | 2,100 | Reference electrical power |
| WATER FLOWS |  |  |  |  |
| water_flow | Cool_Qmax / deltaH × 3600 / 1000 | t/h | 5,732 | Mass flow rate |
| water_vflow | water_flow × 1 | m³/h | 5,732 | Volumetric flow (ρ = 1 t/m³) |
| watermu_CT | 0.00085 × 1.8 × water_vflow × range | m³/h | 8.8 | Makeup water |
| ECONOMICS |  |  |  |  |
| Annuity | i(1+i)ⁿ / ((1+i)ⁿ − 1) | — | 0.06646 | Capital recovery factor |
| CTCost | Guthrie correlation | EUR | Computed | Tower capital cost |
| Cinv2_CT | CTCost × (CEPCI_2020 / CEPCI_2008) × Annuity | EUR/y | Computed | Annualized cost (CEPCI ratio = 1.0362) |

## 5. Implementation Recommendations

### 5.1 Proposed Lua Code for Wet-Bulb Temperature

Replace the hardcoded Twetbulb parameter with a calculated value:

Twetbulb = {job = 'Tdrybulb * math.atan(0.151977 * math.sqrt(RelatHum + 8.313659)) + math.atan(Tdrybulb + RelatHum) - math.atan(RelatHum - 1.676331) + 0.00391838 * RelatHum^1.5 * math.atan(0.023101 * RelatHum) - 4.686035', unit = 'C'},

This ensures that if Tdrybulb or RelatHum changes for different site conditions, Twetbulb — and therefore approach — will update automatically.

### 5.2 Sanity Checks and Validation

Add the following assertions or warnings to the model:

- Approach > 0: Cool_Tin must always be greater than Twetbulb. If not, the cooling tower cannot physically achieve the specified cold water temperature.

- Range in realistic bounds: Typical industrial cooling towers operate with range = 5–15 K. Values outside this range may indicate an error in the process specification.

- Approach in realistic bounds: Typical approach = 3–12 K. Approaches below 3 K are technically feasible but economically expensive; approaches above 15 K suggest inefficient tower design.

Document generated for cooling tower thermodynamic modeling and cost estimation.